## Slide 1: Patient-to-Power Triage
Every litre of diesel should reach the patient who can't wait
ENERGY SIMTECH'26 · Track 3: Open Innovation
Notes: Open with the one-line idea. When the hospital runs on a generator that is too small, our software decides where the limited power and diesel should go, patient by patient.

## Slide 2: The whole project, told to a 5-year-old
1. The big light goes out
At night the hospital's electricity from the city stops.
2. A small helper wakes up
A diesel generator starts, but it can only power about half the rooms, and its fuel runs out.
3. Some children can't wait
Some patients need machines to breathe or stay warm. Others are only using a fan.
4. Our app is a smart helper
It says: keep power where those patients are, move them to lit rooms, switch off empty rooms.
So the diesel lasts longer, and the patients who need power most always get it.
Notes: This is the version everyone on the team must be able to say without notes. Power is like sweets: there are not enough for everyone, so the children who need them most get them first, and nobody wastes sweets on an empty room.

## Slide 3: The problem: too little backup power
40–70%
of normal demand is all the generator can carry in our tests
18%
of generator power goes to empty rooms under today's fixed list
34 / 52
life-support patients powered by today's list on our example night
Today staff switch off whole departments from a fixed list. The list doesn't know a ventilated patient is in a general ward because the ICU is full.
After Hurricane Katrina, about 215 patients died in New Orleans hospitals and nursing homes, partly because generators failed.
It is an energy problem: limited diesel and generator power sent to the wrong places.
Notes: 40-70% is the range used in our simulation, not a national statistic. The 18% and 34 of 52 come from our simulated hospital. Present Tijuana and Sudan only as reported, disputed cases.

## Slide 4: Our solution: five tools in one app
Power plan
Which circuits to keep, which to cut, which surgeries to delay
Move check
Moves patients to powered rooms, and only if a powered lift can carry them
Danger clock
Who loses power first, in minutes
What-if test
Re-plans if a generator fails, fuel is lost or the tanker is late
Pre-outage check
Finds wards and lifts that are not really wired to the generator
Advisor only: it suggests, staff decide. No new hardware. Works from an Excel sheet.

## Slide 5: How it works, end to end
Hospital data
Excel or fake hospital
5 tables
Rules
rules.yaml
priority points
Planner
OR-Tools optimiser
plan_optimal()
Plan
keep / cut / move
/ delay
Screens
dashboard, map,
clock, evidence
Side by side: the same data also goes to plan_baseline(), today's fixed list. The simulation runs both on 50 nights and compares them.
In kid words: We write down who is where, ask the smart helper, and show the answer as a coloured map.

## Slide 6: Every part, explained
One slide per file. Each one has the functions inside it and a kid-words line.

## Slide 7: Data: who is where, on which wire
Table | What one row means
circuits | a power line: kW, breaker limit, on the generator or not
rooms | a room: floor, beds, which circuit feeds it
patients | a patient: room and devices (ventilator, monitor ...)
surgeries | a theatre: surgery running or waiting
generator | size, diesel, expected outage, tanker arrival
Functions
make_hospital()
builds the fake 200-bed government hospital (data/generate.py)
patient_needs()
turns devices into kW, points, battery, life support yes/no
from_excel() / to_excel_bytes()
read an uploaded workbook / write the template
load_rules(), device_list()
read rules.yaml; split "ventilator;monitor"
In kid words: It is a big list: every child, which bed, which machine, and which wire gives that bed electricity.

## Slide 8: rules.yaml: how many points each patient gets
Device | Power | Battery | Points | Life support
Ventilator | 0.25 kW | 30 min* | 100 | yes
Incubator / warmer | 0.60 kW | 0 | 90 | yes
O₂ concentrator | 0.35 kW | 0 | 80 | yes
Inotrope pump | 0.03 kW | 120 min | 70 | yes
Dialysis | 1.50 kW | 0 | 60 | no
Suction | 0.20 kW | 0 | 40 | no
Monitor | 0.06 kW | 60 min | 20 | no
Unknown device | 0.30 kW | 0 | 100 | yes (safe)
A patient's points = their most important device
Unknown device = treated as life support until a nurse confirms
Also sets: generator max 95%, 10% fuel reserve, move penalty
Example values. Doctors must approve them
* 30% of ventilators in the fake data have no working battery
In kid words: Each machine gets stars. A breathing machine gets the most stars, so it gets power first.

## Slide 9: fuel.py: how fast the diesel disappears
Fuel (litres per hour) = 0.08145 × generator size kW + 0.246 × load kW
burn_rate(load, rated)
litres per hour at this load
300 kW set at 250 kW → 85.9 L/h
runtime_h(fuel, load, rated)
hours until the tank is empty
800 L ÷ 85.9 L/h → 9.3 h
fuel_safe_load(fuel, hours, rated)
biggest load that still lasts the hours needed
the planner's target load
In kid words: The engine drinks a little diesel just to stay awake, and more for every light it keeps on.

## Slide 10: baseline.py: today's fixed list (what we beat)
1. fire
2. theatres
3. ICU
4. NICU
5. ER
6. oxygen
7. dialysis
8. cold chain
9. pumps
10. lab
11. wards
12. radiology
13. kitchen
14. lifts
15. OPD
16. corridors
17. laundry
18. admin
plan_baseline(): keep circuits in this order until the generator is 95% full; skip any not wired to it.
Its three blind spots: it doesn't know where life-support patients are (wards come 11th), it never moves anyone, and it ignores fuel.
In kid words: It's like always feeding the same rooms first, even if the hungry child is sitting in a different room.

## Slide 11: planner.py: the smart helper's rules
plan_optimal() decides
Keep each circuit on: yes or no?
Move each high-need patient: where to?
Solved by Google OR-Tools CP-SAT in about 0.1 s
No answer possible? plan_greedy() gives a best-effort plan
9 rules it never breaks
1. Every patient ends up in exactly one place
2. Circuits not wired to the generator stay off; fire lighting and running surgeries stay on
3. Total load ≤ 95% of the generator
4. Each circuit within its breaker
5. Never more patients than beds
6. Right room type (newborns, ventilators); ICU patients only to ICU beds
7. Patients in surgery or on dialysis are not moved
8. Another floor only if a powered lift exists (move check)
9. Patients only move into rooms that stay on
In kid words: The helper has rules it never breaks, like 'never put more children than beds' and 'never use a broken lift'.

## Slide 12: planner.py: how it scores a plan
+ points
for every powered patient (ventilator 100, monitor 20 ...)
+ value
for vital non-patient loads: oxygen plant 60, blood bank 40, pumps 25
− 0.1 / kW
small cost for every kW of diesel burned
− 1.5 / kW
above the fuel-safe load, so the diesel lasts until the tanker
− 5
for each patient move (moves take staff time and carry risk)
Worked example
A ward circuit uses 8 kW. Cost ≈ 8 × 1.6 = 13 points
One ventilated patient on it is worth 100 points
100 > 13, so the ward stays on
An empty admin AC (30 kW, value 1) costs more than it is worth, so it goes off
In kid words: Every plan gets a score. The helper tries thousands of plans and picks the one with the most stars.

## Slide 13: plan.py: reading the answer
Function | What it gives back
Plan | the answer: kept circuits, where each patient ends up, moves, delayed surgeries
circuit_loads() | kW on every circuit after the plan (0 if cut)
patient_status() | for every patient: final room, powered yes/no, moved yes/no
summarize() | the headline numbers: kW kept, diesel L/h, runtime, life support powered
nonessential_kw() | power wasted on empty theatres, offices, corridors
delayed_surgeries() | waiting surgeries whose theatre is switched off
lift_powered() | is any lift on the generator and kept on?
In kid words: These read the helper's answer and count: how many children have light, how much diesel is left.

## Slide 14: Danger clock, pre-outage check, what-if
danger_clock()
danger_clock.py
Minutes until each patient's device loses power
Cut circuit → battery only
Kept → until the diesel runs out
Red < 30 min, amber < 2 h
precheck()
precheck.py
Run on a normal day
Life support on a circuit with no backup
Lifts with no backup, no evacuation route
Overloads, weak batteries, fuel short, missing data
apply_whatif()
whatif.py
Copies the hospital and makes it worse
Lose generator %, lose fuel %
Outage longer, tanker late
Then re-plan and compare
In kid words: A timer shows who is in a hurry, a checker finds broken wires early, and a 'what if' game practises bad days.

## Slide 15: run_sim.py: testing on 50 different nights
Function | Job
make_scenario() | builds one random night: census, faults, generator, fuel, outage
blackout_hours() | how long the generator is off because the tank is empty
evaluate() | scores one plan against what really happened
run_all() | 50 nights × both methods → results.csv
summarize_results() | totals and averages for the Evidence tab
What changes each night
Beds filled 70–110%
Generator 40–70% of demand
Fuel 40–100% of the tank
Outage 2–24 h, staff guess ±30% wrong
Tanker 6–18 h
Random wiring faults
Plus ±20% sensitivity runs (200 more nights)
In kid words: We play the same bad night 50 different ways and see who did better: the old list or our helper.

## Slide 16: app.py, ui.py, tests: what judges see
Live demo
colour map, 3 clicks
Plan details
keep/cut table, moves, printable plan
Danger clock
who runs out first
What-if
sliders for bad days
Pre-outage check
problems + fixes
Evidence
50-night charts
Hospital data
edit or upload Excel
31 tests
prove no hard rule breaks
ui.py draws the cards and hospital_map(). export_static.py makes the one-page web version.
In kid words: These are the pictures and buttons, plus robot checkers that make sure the helper never cheats.

## Slide 17: Results: 50 nights, today's list vs our plan
Chart: % reduction vs today's fixed list
| Life-support patient-minutes without power | Life-support patients cut off at start | Stranded upstairs with no lift | Generator power wasted on empty rooms | Full-blackout minutes | Diesel burn per hour
Reduction vs fixed list (%) | 42 | 81 | 79 | 76 | 27 | 10
50 / 50
nights where our plan was as good or better (better in 44, tied in 6)
In 200 extra ±20% nights it lost 3 times, when the outage guess was wrong. Say this honestly.
In kid words: On 50 pretend nights, our helper kept more children's machines running and wasted less diesel.
Notes: All numbers from sim/results.csv, seeds 1000-1049. These are simulation results with fake data.

## Slide 18: Energy impact, per hour of outage
11.3 L
diesel saved every outage hour (−10%)
≈ ₹1,017
saved per outage hour at ₹90/L
30 kg
CO₂ avoided per outage hour (2.68 kg/L)
+1.3 h
more runtime from every full tank
Honest note: total litres fall only ~4%, because our generator keeps running longer (fewer blackouts).
In kid words: We stop giving diesel to empty rooms, so the same tank lasts longer and makes less smoke.

## Slide 19: The demo in 3 clicks
1
Today: fixed list
34 / 52 life support powered
44 kW wasted on empty rooms
red flashing dots in wards
2
Our patient-aware plan
52 / 52 powered
0 kW wasted
2 moves out of the isolation ward
3
Generator set 2 fails
our plan: 44 / 52 powered
today's list: 21 / 52
diesel lasts 17 h
Then open Evidence (50 outages) for the proof.

## Slide 20: Honest limits and tough questions
Say these before judges ask
Simulation with fake data, not a real hospital
Advisor only: staff decide
Points are examples; doctors approve
Switching is per circuit, not per bed
Generic fuel curve; use the real datasheet
Hospitals already have backup branches by code
Those are fixed when wired. We adapt to tonight's patients and fuel, and find wiring that isn't to code
Moving ventilated patients is risky
Only into powered rooms, ICU to ICU only, with a powered lift; it flags when to bag by hand
Why not a bigger generator?
Costs lakhs and months. Ours is nearly free and helps when a generator fails
Is the test biased?
Same data for both; we report ties, 3 losses and the small 4% litre saving

## Slide 21: Check yourself: every member answers these
1
What problem do we solve, in one sentence?
2
What are the 5 tables of data?
3
Why does a ventilator get 100 points?
4
What does fuel_safe_load() calculate?
5
Name 3 of the 9 rules the planner never breaks
6
Why does the fixed list leave patients without power?
7
What does the pre-outage check find?
8
What are our 3 headline numbers?
In kid words: If every one of us can answer all 8 without looking, we really understand our project.
Notes: Answers: 1 When the generator is too small, we send power and diesel to the patients who need it most. 2 circuits, rooms, patients, surgeries, generator. 3 Without power the patient cannot breathe. 4 The biggest load that still lets the diesel last until the tanker arrives. 5 See the planner rules slide. 6 It switches off by department order and doesn't know where patients are. 7 Life support or lifts not wired to the generator, overloads, weak batteries, fuel shortage, missing data. 8 -42% life-support patient-minutes without power, power wasted on empty rooms 18% to 4%, -10% diesel per hour.

## Slide 22: Power should reach the patient who can't wait
Free, open-source, no new hardware · works from an Excel sheet · staff make the final call